## site's reading
`
Site Name: | [7 empty] | Site Code: | [7 empty] | Date:
Eng.Name: |  | mohamed gabr | [5 empty] | Tech. Name: |  |  |  |  | moharm foad |  |  | Time in: |  | 10:00:00 AM
OMC Eng: | [7 empty] | Tech. Name: |  |  |  |  | ahmed saeed |  |  | Time Out: |  | 13:00
Electrical Installation
Power Supply
Value
KWH meter reading
KVARH meter reading | [10 empty] | NA
[11 empty] | OK | NOK | NA
Check all Earth of shelter | [10 empty] | ok
Tighten the connection | [10 empty] | ok
Check Meter Boxes' sealing, corrosion & open. | [10 empty] | ok
Measurements: | [10 empty] | Value
Neutral / Phase 220 V | [10 empty] | 184.2 | 194.5 | 203
Earth / Phase 220 V | [10 empty] | 189.7 | 189.8 | 200.5
Phase / Phase 380 V | [10 empty] | 335.7 | 334.9 | 330.8
Neutral / Earth | [10 empty] | 0.549
AC current /phase |  |  | (Amp) | [7 empty] | 15.37 | 13.38 | 25.8
Neutral Current |  |  | (Amp) | [7 empty] | 7.3
[11 empty] | OK | NOK | NA
Phase failure protection circuit exist ( Surge Arrestor ) | [10 empty] | ok
[11 empty] | OK | NOK | NA
All Surge Supressor are OK ( OK OR NOK with No of Fault ) | [10 empty] | ok
[11 empty] | Yes | NOK
Are you relocated Surge arrestor Panel | [11 empty] | NOK
| Power Cabinet | [9 empty] | Power Cabinet # I | [5 empty] | Power Cabinet # II
Cabinet | [11 empty] | Type | [5 empty] | Type
Rectifier Type: (Saft Analog/Saft Digital/Lorain/Ascom/Other) | [10 empty] | DELTA2
[11 empty] | OK | NOK | NA |  |  |  | OK | NOK | NA
The 3 input phases connected to the cabinet | [10 empty] | ok
Power cabinet chasses connected to site ground | [10 empty] | ok
Positive output (0 vdc) connected to site ground | [10 empty] | ok
Rectifier Settings
|  | Ibatt | [8 empty] | 0
Tcoeff
[11 empty] | OK | NOK | NA |  |  |  | OK | NOK | NA
|  | Major alarm appeared when battery rack disconnected | [8 empty] | ok
Retighten all Power & DC Cables | [10 empty] | ok
Check rectifier alarms cables connected to DDF | [10 empty] | ok
Machine Labeling: |  |  |  |  | Fuses / dc circuit breakers | [5 empty] | ok
[5 empty] | Alarm cable | [5 empty] | ok
[5 empty] | 48 v cables | [5 empty] | ok
[5 empty] | Rectifier cabinet | [5 empty] | ok
[5 empty] | Battery strings | [5 empty] | ok
Number of operating modules installed | [10 empty] | 6
[11 empty] | OK | NOK | NA |  |  |  | OK | NOK | NA
Minimum 3 modules connected to 3 different phases | [10 empty] | ok
All modules are output balanced | [10 empty] | ok
Check present alarms on rectifier module #1 | [10 empty] | ok
Check present alarms on rectifier module #2 | [10 empty] | ok
Check present alarms on rectifier module #3 | [10 empty] | ok
Check present alarms on rectifier module #4 | [10 empty] | OK
Check present alarms on rectifier module #5
Check present alarms on rectifier module #6
Check present alarms on rectifier module #7
Check present alarms on rectifier module #8
Check present alarms on the rectifier controler | [10 empty] | ok
Check present alarms in the OMC-R | [10 empty] | ok
[11 empty] | OK | NOK | NA |  |  |  | OK | NOK | NA
Lorain rectifier on Normal or Inhibit mode? | [12 empty] | NA
Ascom rectifier tmperature sensor inserted between batteries | [12 empty] | NA
Rectifier tmperature sensor inserted between batteries | [12 empty] | NA
All rectifier measurements from rectifier internal bus bar | [10 empty] | Value | [5 empty] | Value
Positive dc (0 vdc) / Ground | [10 empty] | 0
Negative dc (-48 vdc) / Ground | [10 empty] | -54.5
Set the rectifier to the equalize mode then check the output
Positive dc (0 vdc) / Negative (-48 vdc) | [10 empty] | -54.5
Rectifier Cables
[11 empty] | OK | NOK | NA |  |  |  | OK | NOK | NA
Cables between rec. & batteries are short as possible | [10 empty] | ok
Cables between rec. & batteries are equal in length | [10 empty] | ok
Cables between rec. & batteries are equal in thickness | [10 empty] | ok
Cables between strings are equal in length | [10 empty] | ok
Cables between strings are equal in thickness | [10 empty] | ok
Rectifier Batteries
[12 empty] | Type | [5 empty] | Type
Battery brand (Espace_RG/Powerfit/PowerSafe/EHPC/AGM/Marathon)
Number of batteries connected to the rectifier
Battery nominal voltage
Battery ampere hour
Number of strings
Number of racks
Battery racks are connected to site ground | [10 empty] | OK
Battery racks are fixed to shelter ground | [10 empty] | OK
Number of intercell covers missing | [10 empty] | 0
Separate distance exist between batteries (1 cm) | [10 empty] | OK
Batteries are assembled according to specs | [10 empty] | OK
All batteries are well tightened | [10 empty] | OK
Clean batteries surface using a small moisten texture
All batteries are surface clean | [10 empty] | OK
Clean batteries poles if a residues exist using a solid brush with a solution of baking soda and water or isopropyl alcohol
All battery poles are clean
GEDP
[11 empty] | OK | NOK
Check All terminals within GEDP | [10 empty] | OK
Main GEDP C.B Type | [10 empty] | Normal | Normal |  |  | RCCB
Check All cables (commensurate with load or no) | [10 empty] | OK
[11 empty] | OK | NOK | NA
Check panel fixation | [10 empty] | OK
[11 empty] | OK | NOK
Check C.B rate commensurate with load or no | [10 empty] | OK
[11 empty] | OK | NOK | NA
Check circuit diagram correspond | [10 empty] | OK
[11 empty] | OK | NOK
All component must be fixed at panel | [10 empty] | OK
Remove any duplicated terminals connection | [10 empty] | OK
Remove any welding cables in GEDP duct | [10 empty] | OK
[11 empty] | OK | NOK | NA
24Hr timer adjusted every 4Hr | [10 empty] | OK
Check A/Cs control fuse | [10 empty] | OK
Check all component labels | [10 empty] | OK
[11 empty] | OK | NOK
State of General appearance of GEDP | [10 empty] | OK
Air conditioning
Number of Air conditioning units
[8 empty] | A/C 1 |  |  | A/C 2 |  |  | A/C 3
Type of Air conditioning unit
Capacity of Air conditioning unit (BTU)
Fereon Pressure
Compressor Model
Compressor Type
Compressor Horse power
Output A/C 1 Flow Temperature
Output A/C 2 Flow Temperature
[11 empty] | OK | NOK
| All parts Within A/C are Original | [9 empty] | OK
| Did Main Power Source connected to ODU That supply IDU | [9 empty] | OK
| Cable Thichness are Suitable for Load ( 4mm for 3 HP & 6 mm for 5 HP) | [9 empty] | OK
Fire Panel & Sensors
Radio Shelter:
Fire Panel Type | [5 empty] | ZETA
No of Heat Sensors | [5 empty] | 1
No of Smoke sensors | [5 empty] | 1
No of Flame Sensors
[11 empty] | OK | NOK
Check Fire panel Operation | [10 empty] | OK
Check Batteries of F.P | [10 empty] | OK
Check Terminals of F.P cable | [10 empty] | OK
Fire Panel must be away from any Power source ( GEDP & Rectifier ) | [10 empty] | OK
Are you relocated F.P ? | [11 empty] | NOK |  |  | If No add reason |  | Not exist
Generator Shelter:
Fire Panel Type
No of Heat Sensors
No of Smoke sensors
No of Flame Sensors
Fire Extinguishers
Inside Radio shelter:
| Fire Extinguisher Type (Powder or CO2) | [8 empty] | CO2
| Fire Extinguisher Brand ( Bavaria,…) | [8 empty] | BAVARIA
| Fire Extinguisher Capacity (Kg) | [8 empty] | 6KG
| Fire Extinguisher S/N | [8 empty] | S
| Fire Extinguisher maintenance date | [8 empty] | 2024-05-01
[10 empty] | OK | NOK
| Fire Extinguisher Fixed & Earthed | [8 empty] | OK
Inside Generator shelter:
Number of extinguishers
Fire Extinguisher Type (Powder, Matic or CO2)
Fire Extinguisher Brand ( Bavaria,…)
Fire Extinguisher Capacity (Kg)
Fire Extinguisher S/N
Fire Extinguisher maintenance date
Radio Equipments (BTS , Node-B,…..etc.)
BTS
Number of PCM fed the site
BTS type & model
Number of Sectors
Number of BTS cabinets:
Number of antennas /sector
BTS's Configuration in the OMC
Number of existing Tx Rx boards
Model of existing Tx Rx boards
Number of existing ANYG/Combiners boards
Model of existing Combiner boards
Number of existing NIU boards
Model of Clock boards
Boards Missing
Cables Missing
Radio Equipment
Internal active alarm
|  | VSWR |  | Sect 1
Sect 2
Sect 3
Sect 4
3G
Nokia Siemens
NSN Node B
N of sectors
System module1
Transmission module
RF module 1
RF module 2
Huawei
NodeB type
No of sectors
BBU type
RRU type
Transmission Equipment checklist
[9 empty] | link Power |  | Frequancy |  | Capacity |  | Channel | ADM | Connector check and type |  | NMS |  | SDH | IF status | Check link Budget
Link Type(ALU,NEC,1+1 or 1+0) |  | Direction To | Dish diameter |  | No of ODU |  | ODU TYPE |  | TX | Rx | TX | RX |  | IDU |  |  | IDU | ODU | Cable | Conductivity
| Transmission direction |  |  | PCM NO
|  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8
| Transmission direction |  |  | PCM NO
|  |  |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16
| Transmission direction |  |  | PCM NO
|  |  |  | 17 |  | 18 |  | 19 |  | 20 |  | 21 |  | 22 |  | 23 |  | 24
| Transmission direction |  |  | PCM NO
|  |  |  | 25 |  | 26 |  | 27 |  | 28 |  | 29 |  | 30 |  | 31 |  | 32
| Transmission direction |  |  | PCM NO
|  |  |  | 33 |  | 34 |  | 35 |  | 36 |  | 37 |  | 38 |  | 39 |  | 40
| Transmission direction |  |  | PCM NO
|  |  |  | 41 |  | 42 |  | 43 |  | 44 |  | 45 |  | 46 |  | 47 |  | 48
Water Penetration
Water Penetration result | [5 empty] | Leak |  |  |  |  | No Leak |  |  |  |  | Not Tested
Leak Source |  |  | Roof |  |  |  | Door |  |  | A/C enterance |  |  |  |  | Feeders |  |  |  | Walls
PM Reports
| Cooling System | [14 empty] | Status |  | Sys Fault
| clean A/Cs IDU and ODU | [14 empty] | ok
| check 27 sensor and 4 hours timer | [14 empty] | ok
| Alarms system | [14 empty] | Status |  | Sys Fault
| check all external alarm | [14 empty] | OK
| Enviroment | [14 empty] | Status |  | Sys Fault
| clean earth bar | [14 empty] | ok
| clean site floor | [14 empty] | ok
| Generator | [14 empty] | Status |  | Sys Fault
| Radio Equipment | [14 empty] | Status |  | Sys Fault
| take capture for links | [14 empty] | ok
| Power System | [14 empty] | Status |  | Sys Fault
| Clean rectifiers and modules | [14 empty] | OK
Diesel Generator
| Generator Log Book |  | NA
[7 empty] | G1 | [5 empty] | G2
Generator Unit
Control Box Supplier
Engine type
Alternator type
Voltage
Power
| Frequency | [7 empty] | Hz | [5 empty] | Hz
| Generator 1 Counter | [7 empty] | Hrs | [5 empty] | Hrs
| Oil Pressure Counter | [7 empty] | PSI | [5 empty] | PSI

## Common checklist
Important Tips
All Metal panels must be IP 65 or 66 Schneider or ETA or IDA or INKOL , Otherwise "Orange approval must be taken before using"
All CBs must be Schneider or Merlin Gerin, Otherwise "Orange approval must be taken before using"
No. | Main item | Sub, Item | Severity | Ok/Not | Teams | Description & Action
1 | Main PWR cable
101 |  | Secured Route , without Junction , Cross section (4X25mm cupper, 4x35mm AL ) , approved brand ( Sweedy , SLICO PLUST ) | Critical |  | NS + PM
102 |  | Protection (Fixed PVC ,Cable tray ,Conduit ) | Critical |  | NS + PM
2 | PWR Meter Panel
201 |  | Fixed , Sealed , , Approved brand , Secured location,earthed | Critical |  | NS + PM
202 |  | Connection tightness by using Terminals , Penetration through Glands | Critical |  | NS + PM
203 |  | Panel Labeled, Door frame , lock , Cable arrangement& Duct with cover | Minor |  | NS + PM
204 |  | NO "wrong , illegal , bypass " Connections | Critical |  | NS + PM
205 |  | NO Missing Parts | Major |  | NS + PM
206 |  | Panel status " rust & Corrosion" | Minor |  | PM | For the fatal corrosion " item 201 will cover it.
207 |  | 3 phases "availability & accuracy " | Minor |  | PM
208 |  | PWR meter & Main CB /63A ,approved Brand , status , Rating | Critical |  | NS + PM
209 |  | Cleaning | Minor |  | PM
210 |  | voltage diff. between N& E < 7V | Minor |  | PM
3 | Sharing Panel
301 |  | Fixed , Sealed , Approved brand , Secured location , earthed | Critical |  | NS + PM
302 |  | Connection tightness by using Terminals , penetration through Glands , no sharp edges , cables are protected | Critical |  | NS + PM
303 |  | Labeled panel, Door frame , lock | Major |  | NS + PM
304 |  | NO wrong Connections or Faulty components | Critical |  | NS + PM
305 |  | Panel status " rust & Corrosion" | Minor |  | PM | For the fatal corrosion " item 301 will cover it.
306 |  | Cleaning | Minor |  | PM
307 |  | Main CB /63A , approved Brand , rating | Critical |  | NS + PM
308 |  | No Missing parts | Major |  | NS + PM
4 | Solar Cells (PV) System
401 |  | Clean (not normal dust) | Minor |  | PM
402 |  | Unit and its panel must be fixed , earthed , sealed | Major |  | PM
403 |  | Label unit/components | Minor |  | PM
404 |  | NO "Components faulty /Components below rate/Wrong connection" | Critical |  | PM
405 |  | Alarms on equipment /reporting to the OMC | Critical |  | PM
406 |  | Cables termination/lugs (AC side), lugs (DC side), tightness | Critical |  | PM
407 |  | Cables organization /NO wrong penetration | Major |  | PM
408 |  | NO Missing Parts | Major |  | PM
5 | Generator
501 |  | Clean (not normal dust) , labels (unit & components) ,Earth plates "cleaning & waxed" | Minor |  | PM
502 |  | Unit fixation , earthed , sealed (to avoid rain, aggregated water, major diesel, major oil, etc…) , without sharp edges | Critical |  | PM
503 |  | Door lock/handle / frame fixation that affects door from open easily or close firmly | Major |  | PM
504 |  | NO Components faulty & below rate | Critical |  | PM
505 |  | NO "wrong , illegal , bypass " Connections | Critical |  | PM
506 |  | Alarms on equipment (excluding ADM) , reporting to OMC | Critical |  | PM
507 |  | Cables protection (e.g. floating/[sharp edges in trays/ducts/conduits]) , Connections tightness by terminals or lugs | Critical |  | PM
508 |  | Cables organization & penetration | Major |  | PM
509 |  | Unit corrosion Status (else trays) | Minor |  | PM
510 |  | NO Missing Parts / stolen | Critical |  | PM
511 |  | status of sound proof / High vibration/noise level (e.g. faulty rubber bases) | Major |  | PM
512 |  | Fire extinguisher status (missing/empty/expired/(safety seal) | Critical |  | PM
513 |  | Fire extinguisher fixation | Minor |  | PM
514 |  | PM intervals " schedule" | Critical |  | PM
515 |  | Civil cracks | Major |  | PM
516 |  | Measurements out of range (V/I/Freq./WT/OP/RPM) | Major |  | PM
517 |  | Exhaust pipes insulation/fixation/kit | Major |  | PM
518 |  | Air breather vapor status | Major |  | PM
519 |  | Filters condition oil/fuel/air | Major |  | PM
520 |  | Oil level & quality | Critical |  | PM
6 | PWR SYS / Staplizer /UPS
601 |  | Clean (not normal dust) | Minor |  | PM
602 |  | Unit must be fixed , earthed , sealed | Major |  | PM
603 |  | Label unit/components | Minor |  | PM
604 |  | NO Components faulty /Components below rate/Wrong connection | critical |  | PM
605 |  | Alarms on equipment (excluding ADM) /reporting to the OMC | critical |  | PM
606 |  | Cables termination/lugs (AC side), lugs (DC side), tightness | critical |  | PM
607 |  | Cables organization /NO wrong penetration | Major |  | PM
608 |  | NO Missing Parts | Major |  | PM
7 | GEDP
701 |  | Fixed , Sealed , earthed , Approved brand , Secured location | Critical |  | NS + PM
702 |  | Connection tightness by using Terminals , penetration through Glands , no sharp edges , cable size, no junctions | Critical |  | NS + PM
703 |  | All Components according to " brands , CB Rates , Status " | Critical |  | NS + PM
704 |  | NO "wrong , illegal , bypass " Connections | Critical |  | NS + PM
705 |  | NO Missing Parts | Major |  | NS + PM
706 |  | labeling , Fixed and not Congested Ducts with cover , Cables Arrangements | Major |  | NS + PM
707 |  | Panel Status "rust & Corrosion" | Minor |  | PM | For the fatal corrosion " item 701 will cover it.
708 |  | Door frame ,lock | Major |  | NS + PM
709 |  | Detectors / sensors for HI temp and smoke - reporting to OMC | Major |  | PM
710 |  | Cleaning | Minor |  | PM
711 |  | Use of 3 phases cupper bar and its isolation from both ends | Major |  | NS
8 | DC Box "Indoor sites"
801 |  | Fixed , Sealed , earthed , Secured location | Critical |  | NS + PM
802 |  | Connection tightness by using Terminals & lugs | Critical |  | NS + PM
803 |  | protection &Cable arrangement | Minor |  | NS + PM
804 |  | Panel Label , Door frame , lock | Minor |  | NS + PM
805 |  | Ducts with cover & not congested | Minor |  | NS + PM
806 |  | no Missing Parts & Cable penetration through glands | Minor |  | NS + PM
807 |  | Panel Status if metal "rust & Corrosion" | Minor |  | PM | For the fatal corrosion " item 801 will cover it.
808 |  | NO "Components faulty /Components below rate " CBs"/Wrong connection" | Critical |  | NS + PM
809 |  | cleaning | Minor |  | PM
9 | Surge Panel
901 |  | CB rating (20A /25KA) | Critical |  | NS + PM
902 |  | Connection tightness by using Terminals | Critical |  | NS + PM
903 |  | Surge Arrestor should be Connected with earth directly | Critical |  | NS + PM
904 |  | NO "faulty Components /Wrong connection | Critical |  | NS + PM
905 |  | Metal panel ,Fixed , Sealed , earthed , Approved brand , Secured | Critical |  | NS + PM
906 |  | Panel location (outside the shelter or far away from any Panels) | Major |  | NS + PM
907 |  | no Missing Parts & Cable penetration through glands | Major |  | NS + PM
908 |  | Panel Status "rust & Corrosion" | Minor |  | PM | For the fatal corrosion " item 905 will cover it.
909 |  | reporting to OMC | Major |  | NS + PM
910 |  | Cleaning , Door frame , lock , panel's label | Minor |  | NS + PM
10 | Cooling Sys.
1001 |  | All units must be " fixed , earthed , | Critical |  | PM
1002 |  | All Penetrations sealed & Through Glands | Minor |  | PM
1003 |  | NO faulty Components / below rating /operation / Missing parts /wrong connections | Critical |  | NS + PM
1004 |  | O/D Status " rust /Corrosion" & must be earthed | Minor |  | PM
1005 |  | Terminals for all connections / | Major |  | PM
1006 |  | water evacuation drain / water leakage | Critical/Minor |  | NS + PM | Minor in case the broken DRAIN sys
1007 |  | no Missing Operational parts | Major |  | PM
1008 |  | labels / organized cables / waxing for plates | Minor |  | PM
1009 |  | Cleaning for all units / | Major |  | PM
1010 |  | Sensor 27 operation ,Alarms , reporting to OMC | Major |  | PM
1011 |  | AC adjustment according to the type of site / ventilation fan must be cleaned " if applicable" | Minor |  | NS + PM
1012 |  | HI vibration | Major |  | PM
1013 |  | not congested Ducts / Tape ACs Hoses | Minor |  | PM
11 | Rectifier
1101 |  | Fixed , earthed | Critical |  | NS + PM
1102 |  | Connection tightness by using Terminals , cables are organized protected from sharp edges | Critical |  | NS + PM
1103 |  | "Panel & CB" Labels , Door frame , lock , Ducts with cover | Minor |  | NS + PM
1104 |  | Rectifier alarms tested with OMC / no alarms in panel | Critical |  | NS + PM
1105 |  | cleaning & no rusty parts | Minor |  | PM
1106 |  | no missing parts | Major |  | NS + PM
1107 |  | CBs Rate (BTS , MW , …… ) | Critical |  | NS + PM
1108 |  | no faulty components ( CB , cards ,…..) | Critical |  | NS + PM
1109 |  | no faulty modules | Minor |  | NS + PM
1110 |  | no wrong connection / secured cable path | Critical |  | PM
1111 |  | Saft/Lorain modules must be balanced (LED display/thermal emission) | Major |  | PM
1112 |  | Modules must be sufficient according to calculations & measurements | Major |  | PM
1113 |  | Module operational status | Minor |  | PM
1114 |  | Float voltage should be adjusted per the batteries manufacturer specs | Critical |  | PM
1115 |  | Batteries charging current unlimited per the manufacturer specs | Critical |  | NS + PM
1116 |  | Rect, readings (0) ,+ve must be connected with earth | Major |  | NS + PM
1117 |  | Temp. sensor location (bet. batteries) | Critical |  | NS + PM
12 | Batteries
1201 |  | Battery rack Fixation | Major |  | NS + PM
1202 |  | strings , rack earthed | Major |  | NS + PM
1203 |  | Batteries status (Carry the site when PWR is OFF) | Critical |  | NS + PM
1103 |  | cables are organized | Minor |  | NS + PM
1204 |  | Connection tightness by using Terminals , cables are organized and protected | Critical |  | NS + PM
1206 |  | no Missing parts | Critical |  | NS + PM
1207 |  | no wrong connection | Critical |  | NS + PM
1208 |  | battery Rack rust /corrosion , strings labels | Minor |  | NS + PM
1209 |  | cleaning | Minor |  | PM
13 | Fire System
1301 |  | Detectors (heat/smoke) status (fixation/damaged/malfunction) | Critical |  | NS + PM
1302 |  | Panel fixation | Critical |  | NS + PM
1303 |  | Components operational status | Critical |  | NS + PM
1304 |  | no missing parts (sensors , …….) | Critical |  | NS + PM
1305 |  | no wrong penetration | Minor |  | NS + PM
1306 |  | Fire alarm operational status "must stop A/Cs and/or generator" | Critical |  | NS + PM
1307 |  | Fire extinguisher status "fixation/missing/empty/expired/safety seal" | Critical |  | NS + PM
1308 |  | Terminals for all connections / Tightness | Major |  | NS + PM
1309 |  | alarms , reporting to OMC | Major |  | NS + PM
1310 |  | panel status (in case metal ) " rust &corrosion " | Minor / Major |  | PM | major in case of the fatal corrosion
1311 |  | no wrong connections | critical |  | NS + PM
1312 |  | cleaning / labels / earthed panel if it is metal | Minor |  | PM
14 | DDF + Eqs
1401 |  | All site alarms test with OMC (door alarm / Fire / HI Temp /operation ) "/ alarms on the equipment " some of them tested in the previous steps" | Critical |  | NS + PM
1402 |  | Arrangement and labeling for alarm cables | Minor |  | NS + PM
1403 |  | cables are organized | Major |  | NS + PM
1404 |  | DDF Fixation , well organized (< 10 krones is major) | Critical/major |  | NS + PM
1405 |  | cover for DDF , Cover for KRONE | Minor |  | NS + PM
1406 |  | equipment must be fixed , earthed | Major |  | NS + PM
1407 |  | Camera SYS installed and working without blocking (if existing) | Critical |  | PM
1408 |  | cleaning | Minor |  | PM
1409 |  | No missing parts | Major |  | NS + PM
1410 |  | No wrong connections | Critical |  | NS + PM
1411 |  | all connections with terminals / tightness | Major |  | NS + PM
1412 |  | all devices are labeled | Minor |  | NS + PM
1413 |  | Components operational status | Critical |  | NS + PM
1414 |  | Cables/Jumpers/Coaxial/FO/PCM penetration | Major |  | NS + PM
1415 |  | Cables termination/lugs (AC side), lugs (DC side) | Critical |  | NS + PM
1416 |  | No rust or corrosion on the existing equipment | Minor |  | PM
15 | Civil Work
1501 | Fence | Fence & guard room status | Critical |  | NS
1502 |  | in case / Metal Fence " must be fixed , not rusty OR Corroded | Minor |  | NS + PM
1503 |  | Fence cracks | Major |  | PM
1504 |  | Barbed wires & support status | Major |  | NS + PM
1505 |  | Fence gate & lock status | Critical |  | NS + PM
1506 |  | Fence light | Major |  | NS + PM
1507 |  | Fence gate sensors and its connection / Tested with OMC | Critical |  | NS + PM
1508 |  | liquid penetration/leakage (e.g. rain, aggregated water, …… | Critical |  | NS + PM
1509 | Antenna support | lightening rod 1.5m at least on top of tower | Major |  | NS
1510 |  | Safety wire status | Critical |  | NS + PM
1511 |  | DC night beacon on top of each tower (towers over 45m another beacon will be installed in the middle of tower) | Major |  | NS + PM
1512 |  | Connectors isolation from both ends | Minor |  | NS + PM
1513 |  | Earth kit status & isolation | Minor |  | NS + PM
1514 |  | Labels of feeders from both sides | Minor |  | NS
1515 |  | Feeders must be" fixed with metal clamps/organized on the vertical path" | Major |  | NS + PM
1516 |  | Maximum bending radius for feeders & jumpers | Critical |  | NS
1517 |  | Tower & mast fixation (members, screws ,washers & nuts) corrosion status | Critical |  | NS + PM
1518 |  | No missing Parts | Major |  | PM
1519 |  | Connections with all antennas , MW,……. Must be tightened | Major |  | PM
1520 |  | No wrong penetration | Major |  | NS + PM
1521 |  | No Faulty Components " members , support ,……. | Critical |  | NS + PM
1522 |  | Anticlimbing door for tower ladder , waring sign & lock , no missing steps | Major |  | NS + PM
1523 |  | Side arms status, earth & fixation | Critical/Minor |  | NS + PM | Critical if rusty and not fixed well
1524 |  | Antennas fixation , earthed | Critical |  | NS + PM
1525 |  | Grillage fixation, earth & grease for screws | Minor |  | NS + PM
1526 |  | Grout under grillage chairs | Minor |  | NS + PM
1527 |  | Equipment slab status and isolation | Minor |  | NS + PM
1528 |  | Palm tree trunk section camouflage (scratch/damage) | Major |  | NS + PM
1529 |  | Palm tree fronds (broken/fallen) | Critical |  | NS + PM
1530 |  | Feeders carrying wire inside the palm tree (condition/tension ) | Major |  | NS + PM
1531 |  | Bolts & nuts of the base (missing/loose/rusty) / NO rust on the TWR units | Major |  | NS + PM
1532 |  | Palm tree base grouting not exist | Major |  | NS + PM
1533 | Shelter | Cleaning | Minor |  | NS + PM
1534 |  | No Missing labels " Shelter or equipment , ……. | Minor |  | NS + PM
1535 |  | No Faulty Components " Panels , | Critical |  | NS + PM
1536 |  | Unit must be fixed/ installed well | Critical |  | NS + PM
1537 |  | Double roof fixation / status | Critical |  | PM
1538 |  | No Rusty panels | Minor |  | PM
1539 |  | Shelter floor is earthed , waxing the earth plates , no sharp edges | Major |  | NS + PM
1540 |  | Lighting , Emergency light , switches , sockets | Minor |  | NS + PM
1541 |  | Cable / feeders penetration transit system ( Roxtec) is sealed / Arrangement | Major |  | NS + PM
1542 |  | Door/frame fixation that affects door from open easily or close firmly | Critical |  | PM
1543 |  | Log Book's holder with site's data / PM previous status (date , action) | Minor |  | PM
1544 |  | Shelter steps status ( not rusty , fixed , earthed ) | Major |  | NS + PM
1545 |  | No Missing Parts (ladder ,……. | Major |  | NS + PM
1546 |  | Door lock/handle that affects door from open easily or close firmly | Critical |  | PM
1547 |  | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) | Critical |  | PM
1548 |  | No fetal panel corrosion | Critical |  | PM
1549 |  | no wrong electric connections | Critical |  | NS + PM
16 | Earth Sys
1601 |  | Site earth system according to specifications | Critical |  | NS
1602 |  | All connections secured properly | Minor |  | NS
1603 |  | Earthing measurement value less than 5 ohms | Major |  | NS
1604 |  | All earth bars & rods are greased & covered with foil / cleaned plates | Minor |  | NS + PM
1605 |  | Using of bi-metal lug when connected aluminum cable on Cupper rod | Minor |  | NS + PM
17 | Cables Protection by Cable trays &Ducts & Conduits " Inside / Outside "
1701 |  | Cable trays (not congested , fixed, earthed , with fixed covers by metal clamps (OD) , not rusty or corroded , without sharp edges) | Critical |  | NS + PM
1702 |  | Ducts , Conduits (not congested , fixed, with fixed covers , without sharp edges) | Major |  | NS + PM
1703 |  | all cables are protected by covered cable tray or ducts (not floating ) | Major |  | NS + PM
1704 |  | Using pre-fabricated elbows | Minor |  | NS + PM
18 | Safety Cage & AC cage & Batteries
1801 |  | Existence of cage for GF site & not secured sites | Critical |  | NS
1802 |  | lock with area number existence & its condition | Critical |  | NS
1803 |  | Compliance with cage design, galvanization status | Critical |  | NS + PM
1804 |  | Cage status ( broken items , lock , corrosion ) | Critical |  | PM
19 | TX Panel& cabinet
1901 |  | Fixed , Sealed , earthed , Approved brand , Secured | Critical |  | NS + PM
1902 |  | Lock of cabinet status | Critical |  | NS + PM
1903 |  | Door & HT alarms operation | Critical |  | NS + PM
1904 |  | Fans proper operation | Critical |  | NS + PM
1905 |  | labels for sensors & sensors cables | Minor |  | NS + PM
20 | MW Link installations
2001 |  | OD unit fixation , earth , label & connector isolation | Critical/Major |  | NS + PM | Critical in case unfixed , not earthed
2002 |  | ID unit fixation, earth & label | Major |  | NS + PM
2003 |  | Cables arrangement & labels | Minor |  | NS + PM
2004 |  | Standard rating for CB | Critical |  | NS + PM
2005 |  | Labels for CB | Minor |  | NS + PM
21 | Radio Eq , Fiber inst.
2101 |  | Radio Equipment (RRU, MHA & RRH,MBO, CBO…..etc.) fixation , labels, connector isolation & earth | Critical/Minor |  | NS | Critical in case unfixed
2102 |  | Fiber cable labels | Minor |  | NS
2103 |  | Fiber cable fixation on tower with clamps | Minor |  | NS
2104 |  | Fiber cable arrangement inside cable tray | Minor |  | NS
2105 |  | Existence of fiber box for extra length of fiber cables | Minor |  | NS
22 | Unused Materials
2201 |  | No Extra material inside & outside | Minor |  | NS + PM
2202 |  | No Flammable junk /trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | Critical |  | NS + PM
2203 |  | No Unused assets | Major |  | NS + PM
23 | Miscellaneous | Field Eng. Can add any other items not covered and its severity as well
2301
2302
2303
2304
2305

## Panorama
Shelter panorama
Inside shelter ( Side 1 ) | Inside shelter ( Side 2 ) |  | Inside shelter ( Side 3 ) | Inside shelter ( Side 4 ) | cabinet all opened | cabinet all opened
Outside shelter ( Side 1 ) | Outside shelter ( Side 2 ) |  | Outside shelter ( Side 3 ) | Outside shelter ( Side 4 ) | cabinet all closed | cabinet all closed
Fence panorama
( Side 1 ) | ( Side 2 ) |  | ( Side 3 ) | ( Side 4 )
NA | NA |  | NA | NA
Fence gate inside | Fence gate outside |  | Small fence gate sensor | Large fence gate sensor
NA | NA |  | NA | NA
Tower panorama
( Side 1 ) | ( Side 2 ) |  | ( Side 3 ) | ( Side 4 ) | Tower from distance | Tower from distance | Tower from distance
Site components
GEDP inside | GEDP outside |  | GEDP circuit diagram | GEDP earth
Surge arrestor | Roxtec 1 |  | Roxtec 2 | Shelter floor
Rectifier & Batteries
Inside Rectifier | Outside Rectifier |  | Rectifier modules | Modules lables
CBs lables | Cables terminals |  | Rectifier earth
Batteries overview | Batteries cleaning |  | Batteries rack earth | Batteries CBs inside rectifier
Air condition
Boath A/C IDUs | Boath A/C ODUs |  | Timer | 27 Sensor | A/C earth
A/C1 IDU terminals | A/C1 ODU terminals |  | A/C1 current reading | A/C1 pressure reading
A/C2 IDU terminals | A/C2 ODU terminals |  | A/C2 current reading | A/C2 pressure reading
Radio equipment
2G BTS cabinet overview | 3G cabinet overview |  | MW Rack overview | 2G DDF inside | Alarm BOX | alarms BOX cable
NA | NA |  |  | NA
3G DDF inisde | MW DDF overview |  | MW DDF overview | MW DDF overview | TX cabinet opened | TX cabinet closed
NA
Power
100A panel inside | 100A panel outside |  | Power meter panel inside | Power meter reading | Power meter panel closed // earthed | sharing panel show all CB and cables | sharing panel closed
Phase 1 reading ( V ) | Phase 2 reading ( V ) |  | Phase 3 reading ( V ) | power cables path | power cables path | power cables path | power cables path
Fire System
Fire panel inside | Fire panel outside |  | Heat zone alarm | Smoke zone alarm | Batteries voltage
Fire Extinguisher | Fire Extinguisher maintenance date |  | Fire Extinguisher safety seal
Earth
Main earth bar | Main earth rod |  | Earth inside shelter | Tower earth | Earth panroama | Earth panroama | Earth panroama
Cable tray
Cable tray 1 inside shelter | Cable tray 2 inside shelter |  | Cable tray 3 inside shelter | Cable tray 4 inside shelter | Outside cable tray | Outside cable tray | Outside cable tray
Cable tray outside shelter ( Down view ) | Cable tray outside shelter ( Upper view ) |  | Inside cable tray earth | Outside cable tray earth | Outside cable tray with tower | Roxtec inside | Roctec Outside
NA
Light system
Emergency light | Shelter light |  | Beacon light | Halogen light | Fence Lighting
NA |  |  | NA | NA | NA
PM logbook

## Tower Panorama
Tower panorama
Sec 1 Antenna Isolation | Sec 2 Antenna Isolation |  | Sec 3 Antenna Isolation | Sec 4 Antenna Isolation
Feeders and Jumpers Systemization ( 1 ) | Feeders and Jumpers Systemization ( 2 ) |  | Feeders and Jumpers Systemization ( 3 ) | Feeders and Jumpers Systemization ( 4 )
MW (1) ODUs+IF Cable Connector Isolation | MW (2) ODUs+IF Cable Connector Isolation |  | MW (3) ODUs+IF Cable Connector Isolation | MW (4) ODUs+IF Cable Connector Isolation
MW (5) ODUs+IF Cable Connector Isolation | MW (6) ODUs+IF Cable Connector Isolation |  | MW (7) ODUs+IF Cable Connector Isolation | MW (8) ODUs+IF Cable Connector Isolation

## Before & after
Before |  | After
Pic #1 | (Mandatory) Item #: | Picture #1
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need clean |  | Done
Pic #2 | (Mandatory) Item #: | Picture #2
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need clean AND COVER |  | Done
Pic #3 | (Mandatory) Item #: | Picture #3
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need clean |  | Done
Pic #4 | (Mandatory) Item #: | Picture #4
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need to clean |  | Done
Pic #5 | (Mandatory) Item #: | Picture #5
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need to clean |  | Done
Pic #6 | (Mandatory) Item #: | Picture #6
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need clean |  | Done
Pic #7 | (Mandatory) Item #: | Picture #7
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need to clean |  | done
Pic #8 | (Mandatory) Item #: | Picture #8
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
need to clean |  | done
Pic #9 | (Mandatory) Item #: | Picture #9
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
NEED CLEAN |  | DONE
Pic #10 | (Mandatory) Item #: | Picture #10
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
NEED CLEAN |  | DONE
Pic #11 | (Mandatory) Item #: | Picture #11
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description
Pic #12 | (Mandatory) Item #: | Picture #12
a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK. |  | a) MS Office 2003: Resize: 1- Double click on picture, select size tab 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Double click on picture, press Compress 2- Select all pictures in document & select Web/Screen 3- Press OK a) MS Office 2007: Resize: 1- Click on picture, select the format tab, on the far right side of the tools bar, change the size. 2- Landscape: 320 Width x 238 Height (Pixels) 3- Portrait: 178 Width x 238 Height (Pixels) Compression: 1- Click on picture, select the format tab on the far left side of the tools bar. 2- Select compress, then press OK.
(Mandatory) Description |  | (Mandatory) Description

## Pending Res.
Pending Reserves
No. | Site Name | Site Code | Reserve | Date
1
2
3
4
5
6
7
8
9
10
11 |  |  |  |  | Reserve 1 | Reserve 2
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26 |  |  |  |  | Reserve 3 | Reserve 4
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41 |  |  |  |  | Reserve 5 | Reserve 6

## unused assets
unused assets
No. | Site Name | Site Code | Reserve | Date
1
2
3
4
5
6
7
8
9
10
11 |  |  |  |  | Reserve 1 | Reserve 2
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26 |  |  |  |  | Reserve 3 | Reserve 4
27
28
29
30
31
32
33
34
35
36
37
38
39

## alarms capture
BTS capture ( Alarms ) | 3G capture | MW capture
BTS capture ( Clear )

## Audit matrix SQI
File | Network Audit Checklist (applicable on entire radio sites)
File Version | V10R00
Department | Technology / Access Network Support / Network Audit
Creator Name | Samer Zaki
Creator Title | Network Audit Manager
Site Name
Site Code
Auditor | mohamed gabr
Audit Date
Area | delta
Maintenance Office | tanta
Contractor
Contractor Area
Contractor Office
Score
Power Meter Condition
Power Meter Reading (KWH)
Site Logbook
Site Last PM Date | dd-mmm-yyyy
Gen. Logbook
Gen. Last PM Date | dd-mmm-yyyy
Standby Gen. Hours Meter Reading
Main System |  | Power System | [62 empty] | Cooling System | [6 empty] | Fire System | [6 empty] | Equipment and DDF | [6 empty] | Civil | [20 empty] | Generator | [6 empty] | Equipment | Vendor | Offender | Assigned Team
System |  | Power Meter & Main Breaker |  |  |  |  | Calc #1 | Calc #2 | Shared Panel |  |  |  |  | Calc #1 | Calc #2 | GEDP |  |  |  |  | Calc #1 | Calc #2 | Surge Arrestor |  |  |  |  | Calc #1 | Calc #2 | DC Boxes |  |  |  |  | Calc #1 | Calc #2 | Rectifiers |  |  |  |  | Calc #1 | Calc #2 | Batteries |  |  |  |  | Calc #1 | Calc #2 | UPS / Stabilizer / Transformer |  |  |  |  | Calc #1 | Calc #2 | Solar Cells (PV) System |  |  |  |  | Calc #1 | Calc #2 | A/Cs Cooling / Free Cooling / Ventilation |  |  |  |  | Calc #1 | Calc #2 | Fire Alarm and Fighting System |  |  |  |  | Calc #1 | Calc #2 | Equipment and DDF |  |  |  |  | Calc #1 | Calc #2 | Shelter Body / Main Enclosure |  |  |  |  | Calc #1 | Calc #2 | Antenna Support |  |  |  |  | Calc #1 | Calc #2 | Fence / Roof |  |  |  |  | Calc #1 | Calc #2 | ATS / Engine |  |  |  |  | Calc #1 | Calc #2
Score Ceiling |  | 5 | [6 empty] | 4 | [6 empty] | 12 | [6 empty] | 10 | [6 empty] | 4 | [6 empty] | 8 | [6 empty] | 5 | [20 empty] | 12 | [6 empty] | 10 | [6 empty] | 7 | [6 empty] | 9 | [6 empty] | 7 | [6 empty] | 7 | [6 empty] | 10
Serial | Items | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable |  |  | Recommendations | Minor | Major | Critical | Accountable | [6 empty] | Total | Minor Exist | Major Exist | Critical Exist | Higher Selection | Score
1 | Clean (not normal dust) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | Label unit/components |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
3 | Panel/cables secured location/route (e.g. Surge panel outside the shelter or far away from other panels) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4 | Approved brand (panel/cable/components) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
5 | Less than 3 phases available (if the power source is 3 phases) |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
6 | Voltage difference between Neutral & Earth > 7 volts |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
7 | Unit unfixed/not installed well |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
8 | Door/frame fixation that affects door from open easily or close firmly |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
9 | Door lock/handle that affects door from open easily or close firmly |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
10 | Liquid penetration/leakage (e.g. rain, aggregated water, major diesel, major oil, etc…) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
11 | Unit sharp edges |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
12 | Unit earth |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
13 | Earth plates cleaned, waxed, covered with foil | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
14 | Bi-metal lugs used to connect Aluminum cable to Cupper rod | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
15 | Components faulty |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
16 | Components below/over rate (excluding main power feeder if not hot) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
17 | Wrong connection |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
18 | Alarms on equipment (excluding ADM) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
19 | Alarms reporting to the OMC | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
20 | Cables/Jumpers/Coaxial/FO/PCM protected in trays/ducts/conduits |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
21 | Cables/Jumpers/Coaxial/FO/PCM organization |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
22 | Cables/Feeders/Jumpers/Coaxial/FO/PCM connection tightness |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
23 | Cables termination/lugs (AC side), lugs (DC side) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
24 | Camera revolved to be blocked (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
25 | Messy DDF (more than or equal to 10 Krone Blocks or equivalent) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
26 | Messy DDF (less than 10 Krone Blocks or equivalent) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
27 | Feeders unfixed/unorganized on the vertical path | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
28 | Feeders without tray on the horizontal path | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
29 | Feeders unorganized on the horizontal path | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
30 | Trays/ducts/conduits congested | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
31 | Trays/ducts/conduits unfixed |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
32 | Ducts/conduits covers missing/unfixed |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
33 | Trays covers missing/unfixed (if laid on the ground only) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
34 | Trays untied by metal belts |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
35 | Trays/Roxtec/Plate not earthed |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
36 | Trays rust |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
37 | Trays corrosion |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
38 | Use pre-fabricated trays elbows for 90 degrees angles (not modified) |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
39 | Unit rust (else trays) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
40 | Unit corrosion (else trays) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
41 | Some parts are (missing / stolen) |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
42 | Equipment slab status and isolation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
43 | Grillage fixation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
44 | Grillage grease for screws | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
45 | Wiring diagram (SLD) unavailable or mismatches the as built | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
46 | Positive output (0 vdc) not earthed | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
47 | Saft/Lorain modules unbalanced (LED display/thermal emission) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
48 | Modules insufficient according to calculations & measurements | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
49 | Module faulty | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
50 | Float voltage unadjusted per the batteries manufacturer specs | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
51 | Batteries charging current unlimited per the manufacturer specs | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
52 | Temperature sensor not inserted between batteries (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
53 | High vibration/noise level (e.g. faulty rubber bases) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
54 | Refrigerant line isolation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
55 | Drain pipes condition & slope | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
56 | A/Cs ATS thermostat sensor (former 27 degree sensor) operation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
57 | A/Cs unadjusted to specified degree | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
58 | Security metal cage broke/faulty lock/non-galvanized/corroded/not complied by Orange design (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
59 | Fire alarm don't stop A/Cs and/or generator | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [12 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
60 | Fire extinguisher missing/empty/expired/(safety seal) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [12 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
61 | Fire extinguisher unfixed | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [12 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
62 | Lights operation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
63 | Emergency light operation & battery condition | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
64 | Light switches & AC outlets (condition & location) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
65 | Unused assets | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
66 | Flammable junk/trash inside/outside (e.g. plastics, papers, cartoon boxes, etc…) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
67 | Non-flammable junk/trash inside/outside (e.g. metals, woods, etc… ) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
68 | Logbook holder & site info (Orange, Site Name, Code, Area, etc..) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
69 | Barbed wire & supports | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [12 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
70 | PM intervals out of schedule | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
71 | Double roof unfixed/broke | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [7 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
72 | Stairs/climbing ladder condition (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [6 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
73 | Anticlimbing door warning sign | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
74 | Ventilation fan clean and function (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [12 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
75 | Feeders earth kit and connectors isolation | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | [6 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
76 | Beacon light function | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
77 | Climbing safety wire | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
78 | Earth connected to antennas & MW ODU | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
79 | Palm tree trunk section camouflage (scratch/damage) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
80 | Palm tree fronds (broke/fall) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
81 | Palm tree base grouting not exist | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [11 empty] | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
82 | Lightening rod 1.5m at least on top of tower (if applicable) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
83 | Feeders carrying wire inside the palm tree (condition/tension ) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
84 | Bolts & nuts of the base (missing/loose) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
85 | Faulty sound proof | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
86 | Measurements out of range (V/I/Freq./WT/OP/RPM) | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
87 | Exhaust pipes insulation/fixation/kit | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
88 | Air breather vapor status | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
89 | Filters condition oil/fuel/air | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
90 | Oil level & quality | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 | [5 empty] | 0 | 0 |  |  |  |  | M | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
Maint | 100 % | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0 | [5 empty] | Maint | 0
Dep | 100 % | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0 | [5 empty] | Dep | 0
Gen | 100 % | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0 | [5 empty] | Gen | 0
Miscellaneous Reserves (not identified above and not weighed):
1
2
3
4
5
Dropdown Lists
Power Meter Condition
Exist & function
Not exist & site powered by gen./solar cells
Not exist & power rented from the owner
Exist & gen. running because power was normally cut during visit
Exist & gen. running because power is frequently unstable
Exist & gen. running because of power cable problem
Exist & gen. running because of wrong phases rotation
Exist & gen. running because EC cut our power
Illegal power
Exist & not connected
Exist & faulty (OOS)
Not reachable
Site/Gen. Logbook
Missing
No PM record found according to the planned schedule
Logbook for the last 8 months exist & the last PM recorded with date
Logbook for the last 8 months exist & the last PM recorded without date
Logbook has records less than 8 months & the last PM recorded with date
Logbook has records less than 8 months & the last PM recorded without date
Equipment
BSC
BTS
PCU
RNC
Cards
Modems
Cables
Empty Racks
MW IDU/ODU
Antenna
Rectifiers
Batteries
UPS
Stabilizer
Civil
Vendor
NSN
HUA
E///
NEC
ALU
MOTO
Transmission Solutions
ZTE
UniPower
Production
Score
Minor | 2
Major | 5
Critical | 10
Note on CE51: Suggested modification: Critical